ΒΕLLOWS SEALED VALVES PN25

Bellows sealed globe valves with stainless steel bellows and flanges according to EN 1092-2-B PN25.

They will consist of nodular cast iron body and bonnet EN-GJS-400-18-LT and shall have face-to-face length according to EN 558-1 Series 1. Their maximum operating temperature will be 350οC. They shall have non-rising stem, with hand-wheel with opening limiting screw, lubricator and mechanical proportional position indicator.

The bellows will be multi-layered, made of titanium stainless steel 1.4541 (AISI 321), designed for a long service life, with a minimum life cycle as per MSS SP-117 and will be equipped with a non-turn system. The bellows will be attached to the shaft and not to the disc, in order to avoid vibration transmission to the bellows and ensure a longer service life.

The disc will be of conical plug type and shall rotate freely 360° for better centering on the seat and cleaning of dirt or impurities fluids may carry, allowing a tighter shut-off, while avoiding vibrations from being transmitted to the stem. Both the plug and the seat shall be hard faced 13% Cr and will ensure tightness according to EN 12266-1 rate A (Zero leakage).

The stem will be stainless steel, with ACME tapered thread and large robust hand-wheel, to ensure easy operation. It must be blowout-proof, with TA-LUFT certified safety stuffing box packing made of pure graphite and a metal back seat to prevent leakage in the open position, even if the bellow and seal are damaged.

The sealing between the body and the upper part shall be achieved with a stainless steel reinforced graphite gasket, housed in tongue and grooved flanges.

The valves will be suitable for use with steam, thermal oil, gases, liquids, water and condensate.

They will be accompanied by a certificate of compatibility with the European Directive PED 2014/68 / EU and certificate EN 10204 3.1 for the body.

Indicative type: BV25063 by BValve